## Summary
DETAILED QUANTITY TAKEOFF — EXTERIOR ELECTRICAL & COMMUNICATIONS
DOE Legacy Management — Site Improvement Package ¦ 764 Horizon Dr., Grand Junction, CO
Basis: 65% Submittal QC set (Kenall-FSC JV / HDR, issue date Sept 02 2026; elec sheets dated Feb 23 2026) — Contract W9128F24D0010. NOT FOR CONSTRUCTION.
Scope per direction: EXTERIOR electrical & communications only (ES/E, TSN, TSY series + CD101 demo). Civil, wet utilities, fire protection & building interior systems excluded.
TOTALS BY SYSTEM
System | Drawing Series | Extension ($) | Remarks
Site Electrical (power, lighting, generator, service, demo) | E-001, ES101, ES601, CD101 | 0 | Utility primary & transformer by Xcel Energy; lighting branch circuits carried as allowance (not drawn at 65%).
Telecommunications OSP (duct banks, MH/HH, fiber) | TSN001, TSN100, TSN300, TSN400 | 0 | Duct bank lengths from plan dims where shown, otherwise scaled at 1"=30'. ISP cabling & pedestal by ISP.
Security (access control, video intercom, gates) | TSY001, TSY002, TSY100, TSY101 | 0 | Video surveillance, intrusion detection, blue phones struck from matrix at 65% — excluded, verify.
PROJECT TOTAL — EXTERIOR ELECTRICAL & COMM |  | 0
HOW TO USE / LEGEND
Yellow cells | Enter your unit costs (material + labor) in the yellow 'Unit Cost' cells; extensions & totals compute automatically.
Blue quantities | Scaled from plan (1"=30') or carried as allowance — expect ±10-20% movement; firm up at 95%.
Orange rows | Open question / QC-comment risk — verify before bid (see notes column).
Size & Type columns | Sizes and types/materials/models are from drawing schedules & details; entries marked '(assumed)' or 'TBD' are not on the 65% drawings — confirm in specs or next submittal.
Basis column | Counted = symbol count from plan · Dimensioned = printed plan dimension · Scaled = measured at 1"=30' · Allowance = not shown at 65% · By Others-NIC = coordination only · Calc = formula-driven from other rows.
Example | e.g. Site Electrical item C1 (EA1 pole light): enter 12,500 in the yellow cell → extension shows $112,500 for 9 poles.
KEY 65% DESIGN GAPS / QC COMMENTS AFFECTING QUANTITIES
1. Site photometric plan to be added (QC on ES101) — fixture counts/locations may change; one EA1 pole flagged for relocation (fire-truck access conflict near relocated generator).
2. Site lighting branch circuiting, panel sources & one-line references are not in the site set — carried as allowances; conduit/wire sizes assumed and so noted.
3. TSN100 duct bank overall dim 508'-8 3/4" at HH1-6 does not reconcile with segment dims (sums ±300 LF) — RFI recommended.
4. TSY002 matrix strikes video surveillance, intrusion detection, WAPs and blue phones, but TSY101 still shows VSS server / 'to building cameras' — confirm deletions.
5. Card reader locations updated per TSY100 at QC; gate-operator power JB may move closer to reader (ES101 QC).
6. Civil background on TSN100/TSY100 to be updated to most current — handhole/pedestal positions (HH1-1 labeling) to be confirmed.
7. OSP copper backbone questioned on TSN300 ('Where is the OSP copper?') — matrix lists it as contractor scope; allowance carried, pair count TBD.
8. Demarcation between Xcel Energy work and contract work to be documented in Design Analysis (QC on ES101) — primary work carried as NIC.
9. Luminaire schedule wattage/lumens/CCT columns largely blank at 65%; transformer kVA, generator kW, and secondary conductor sizes await one-line (building package).

## Site Electrical
SITE ELECTRICAL TAKEOFF (Sheets E-001, ES101, ES601 + CD101 demo)
DOE Legacy Management – Site Improvement Package ¦ 764 Horizon Dr., Grand Junction, CO ¦ 65% Submittal (Issue 02 SEP 2026) ¦ Contract W9128F24D0010
Item | Description | Size | Type / Material / Model No. | Ref (Sheet / Detail / Keynote) | Basis | Qty | Unit | Unit Cost ($) | Extension ($) | Notes
A. DEMOLITION / UTILITY COMPANY COORDINATION
A1 | Remove existing utility primary conduit & conductors back to splice point | Size unknown (existing) | Existing UG primary conduit & cable — remove & dispose | ES101 / KN 2 | Scaled | 50 | LF |  |  | Heavy-hatched route, splice point to existing transformer at Bldg A SW corner. Scaled at 1"=30' (±20%).
A2 | Existing utility transformer demolition — BY UTILITY (Xcel); coordination only | — | Existing pad-mount utility transformer | ES101 / KN 9 | By Others-NIC | 1 | EA |  |  | Demolished by utility company. Carry coordination/scheduling only.
A3 | Relocate existing government-owned generator to Building 'A' site, incl. all testing for manufacturer recertification | Rating TBD (existing unit) | Existing gov't-owned engine generator — rig, relocate, reconnect, recertify | ES101 / KN 8 | Counted | 1 | LS |  |  | Building EC responsible per KN 8. Nameplate/kW not shown in site set — confirm from building package.
A4 | Utility PRIMARY boring/trenching, conduit & wiring, splice point to new transformer — BY XCEL ENERGY | Per XE standards | Primary conduit & MV cable per Xcel Energy standards; 24" min trench, warning tape | ES101 / KN 1,3,4; 1/ES601 | By Others-NIC | 150 | LF |  |  | XE provides all primary conduit/wiring/trenching (KN 4). Route scaled ±150 LF for coordination. EC coordinates routing & termination.
A5 | Remove existing parking lot light pole and foundation (NW parking, Tract I) | Height unknown (existing) | Existing site light pole + concrete foundation — remove & dispose | CD101 / KN 6 | Counted | 2 | EA |  |  | 2 poles at KN 6 arrows. Note ES101 QC also flags relocating one NEW pole near generator — separate issue.
A6 | Remove existing underground electric line (UGE) serving demo'd poles | Size unknown (existing) | Existing UG electric branch — remove & dispose | CD101 / KN 6, legend | Scaled | 200 | LF |  |  | Between/beyond removed poles toward Bldg A. Scaled at 1"=30' (±25%).
A7 | Remove existing underground telephone line (T linetype) | Size unknown (existing) | Existing UG telephone cable/duct — remove & dispose | CD101 legend | Scaled | 400 | LF |  |  | Runs along north frontage/site. VERIFY ownership (telco may remove own plant) and limits.
A8 | Demolish existing electric meter | — | Existing utility meter — demolish, coordinate w/ XE | CD101 legend (EM) | Counted | 1 | EA |  |  | Legend item; symbol at Bldg A service area. Verify count at 95%.
A9 | Demolish existing communications junction box | — | Existing comm JB — demolish | CD101 legend | Counted | 1 | EA |  |  | Legend item; verify count. Comm pedestal at NW corner of Bldg C to be PROTECTED (QC fence-removal comment).
A10 | Protect in place: (2) existing transformers & pads, existing overhead power & poles (south boundary), comm pedestal at Bldg C | — | Temporary protection / barricades / coordination | CD101 notes | Counted | 1 | LS |  |  | Any utility damaged repaired at no additional cost (CD101 GN 1).
| Subtotal A | [7 empty] | 0
B. SERVICE & GENERATOR
B1 | New pad-mounted utility transformer — BY XCEL; coordination | 480/277V, 3-phase (kVA TBD by XE) | Pad-mount, XE-furnished & installed; XE makes primary & secondary connections | ES101 / KN 4 | By Others-NIC | 1 | EA |  |  | kVA sizing by utility from building load letter — not shown in site set.
B2 | Transformer concrete pad w/ clearances per XE | Per XE standard dwg | Cast-in-place concrete pad + ground grid per XE requirements | ES101 / KN 4 | Counted | 1 | EA |  |  | Pad by GC per KN 4 — coordinate pad & clearance requirements with XE.
B3 | Utility meter housing (furnish & install, coordinate w/ XE) + CT cabinet | Per XE metering std | Meter housing + CT cabinet, NEMA 3R; meter device by XE | ES101 / KN 4 | Counted | 1 | EA |  |  | EC furnishes & installs housing; XE furnishes/installs/connects meter.
B4 | UG secondary conduit system, transformer to Bldg A main service disconnect / MDP | Conduit qty & size TBD per one-line | PVC Sch 40 (assumed) w/ XHHW-2 Cu secondary conductors per one-line | ES101 / KN 5 | Scaled | 30 | LF |  |  | One-line is in building package — verify conduit count/size & conductor schedule at next submittal.
B5 | UG conduits, generator to automatic transfer switch(es) | Conduit qty & size TBD per one-line | PVC Sch 40 power + control (assumed); stub-ups field coordinated | ES101 / KN 6 | Scaled | 50 | LF |  |  | Refer to one-line for conduit count. Field coordinate exact routing & stub-up locations prior to rough-in (KN 6).
| Subtotal B | [7 empty] | 0
C. SITE LIGHTING (Schedule & details ES601)
C1 | Fixture EA1 — pole-mounted LED area light, Type 3 backlight control, glare shield, house-side shield, w/ pole | 35' pole; 277V; 3000K, 80 CRI | Lithonia DSX1-LED-P3-30K-80CRI-BLC3-MVOLT-PIR-SPD20KV-HS-EGSR-DDXX | ES101/ES601 sched. | Counted | 9 | EA |  |  | Tag count from plan. Integral PIR motion, dims to 30% after 10 min. Wattage/lumens columns blank in 65% schedule.
C2 | Fixture EA2 — pole-mounted LED area light, Type 5 wide distribution, glare shield, w/ pole | 35' pole; 277V; 3000K, 80 CRI | Lithonia DSX1-LED-P3-30K-80CRI-T5W-MVOLT-PIR-SPD20KV-EGSR-DDXX | ES101/ES601 sched. | Counted | 7 | EA |  |  | 7 tagged poles; plan symbols show TWIN heads on EA2 poles — verify heads/pole (14 luminaires if twin). Priced per pole assembly.
C3 | Fixture EA3 — pole-mounted LED area light, short-throw (T1S) distribution, glare shield, house-side shield, w/ pole | 35' pole; 277V; 3000K, 80 CRI | Lithonia DSX1-LED-P3-30K-80CRI-T1S-MVOLT-PIR-SPD20KV-HS-EGSR-DDXX | ES101/ES601 sched. | Counted | 2 | EA |  |  | Tag count from plan (east parking).
C4 | Pole base foundation w/ anchor bolts, grout, ground stud, handhole access | 2'-0" dia. x 9'-6" deep | CIP concrete (Div 03); 8-#5 vert., #4@10" ring ties; round in unpaved / square at paving | 2/ES601 dim. sched. | Counted | 18 | EA |  |  | 31'-40' pole row of dimension schedule governs for 35' poles.
C5 | Ground rod & pole bond | 5/8" x 8' rod (assumed — not sized on dwg) | Cu-clad steel rod; #6 AWG bare Cu bonded to rebar & pole ground stud | 2/ES601 | Counted | 18 | EA |  |  | One per pole base per detail. Rod size to be confirmed in Div 26 specs.
C6 | Fixture EB1 — exterior LED bollard (RADEAN), at grade | 8-1/4" dia x 41-1/2" H; 277V; 3000K, 80 CRI | RADB-LED-P1-30K-SYM-PIR-BTT-BCF-HXX-DDXX (schedule lists 'Luminis'; RADB is a Lithonia/Acuity RADEAN model — see RFI-13) | ES101/ES601 sched. | Counted | 6 | EA |  |  | 6 bollards along Bldg A south walk; integral PIR, symmetric distribution.
C7 | Bollard base foundation | 1'-2" x depth per detail | CIP concrete (Div 03); 4-#5 vert., #3 ties @10"; anchor bolts & leveling nuts per mfr | 3/ES601 | Counted | 6 | EA |  |  | Round foundation in unpaved areas; square in/adjacent to paving.
C8 | Fixture EF1 — exterior flagpole downlight, truck mounted | Size M (flags to 15'x25'); 3000K; remote driver | Eagle Mountain Flag & Flagpole 'StarGazer' SG-3K-EHS-M-XX (external-halyard stationary truck, dark-sky downlight) | ES101/ES601 sched. | Counted | 3 | EA |  |  | 3 at flagpoles NW of Bldg A. Schedule voltage column shows 0V at 65% — driver remote (see C9).
C9 | Weatherproof box w/ remote drivers for EF1 fixtures, buried in adjacent landscaped area | NEMA 4/6P burial-rated (assumed) | WP enclosure + (3) remote LED drivers | ES101 / KN 10 | Counted | 1 | EA |  |  | Field verify exact location of remote drivers prior to rough-in (KN 10).
C10 | Site lighting branch circuits — conduit, conductors & trench (ALLOWANCE — circuiting not shown at 65%) | 1" PVC Sch 40 (assumed), 24" bury | 2#10 + 1#10G Cu THWN-2 (assumed), 277V circuits; warning tape | ES101 | Allowance | 2400 | LF |  |  | No homeruns/circuit routing drawn at 65%; photometric plan to be added per QC. Allowance = pole-to-pole loop + homeruns; revise at 95%.
C11 | Lighting control interface — timeclock via lighting control panel in Bldg A | — | Control/interface wiring to LCP (panel in building package) | ES601 seq. of ops | Allowance | 1 | LS |  |  | Carry site interface/controls wiring allowance.
| Subtotal C | [7 empty] | 0
D. GATE OPERATOR POWER
D1 | Exterior-rated junction box, 120V power connection to exterior gate operator | Size per NEC 314 (min 4-11/16" sq assumed) | NEMA 3R/4 galvanized steel JB, stamped, gasketed | ES101 / KN 7 | Counted | 3 | EA |  |  | One at each vehicle gate (Bldg B west gate + 2 east gate pedestals). Verify exact locations w/ approved shop dwgs. QC: JB may shift closer to card reader.
D2 | Branch circuit to gate operator JBs (ALLOWANCE — source panel/routing not shown) | 3/4" PVC (assumed conduit type) | 2#10 + 1#10G Cu, 120V per KN 7 | ES101 / KN 7 | Allowance | 700 | LF |  |  | Conductors/size per KN 7; conduit material & source panel not indicated at 65%. Allowance for 3 runs.
| Subtotal D | [7 empty] | 0
| SITE ELECTRICAL TOTAL | [7 empty] | 0

## Telecom OSP
TELECOMMUNICATIONS OSP TAKEOFF (Sheets TSN001, TSN100, TSN300, TSN400)
DOE Legacy Management – Site Improvement Package ¦ 764 Horizon Dr., Grand Junction, CO ¦ 65% Submittal (Issue 02 SEP 2026) ¦ Contract W9128F24D0010
Item | Description | Size | Type / Material / Model No. | Ref (Sheet / Detail / Keynote) | Basis | Qty | Unit | Unit Cost ($) | Extension ($) | Notes
A. UNDERGROUND STRUCTURES
A1 | MH1 — telecom maintenance hole w/ cover, duct terminators/knockouts, bonding ribbon (4 plcs), sump | 8'-0" L x 96" W x 96" H; 13" dia sump | Precast concrete, 4260 base (9,275 lb) + 4260 top deck (2,100 lb), traffic-rated cover | TSN100 sched.; H1/TSN400 | Counted | 4 | EA |  |  | MH1-1 thru MH1-4. Provide knockouts to avoid 90° turns in duct bank (TSN400 note).
A2 | HH1 — telecom handhole | 3'-0" L x 24" W x 48" H | Polymer concrete box w/ slip-resistant polymer concrete cover, fasteners — NOT vehicle-traffic rated | TSN100 sched.; A1/TSN400 | Counted | 5 | EA |  |  | HH1-2 thru HH1-6 on TSN100. Install ≥5' from building perimeter (KN 2/3).
A3 | HH1-1 handhole (appears on TSY100 security plan only — VERIFY if additional) | 3'-0" x 24" x 48" | Polymer concrete (same as A2) | TSY100 | Counted | 1 | EA |  |  | TSY100 labels an HH1-1 near Horizon Dr. not tagged on TSN100 — confirm 6th handhole vs. re-label.
| Subtotal A | [7 empty] | 0
B. DUCT BANKS (schedule TSN100; sections TSN400)
B1 | DB1 duct bank — MH1-1 to ISP telecom pedestal (east along Horizon Dr.) | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 / KN 1 | Scaled | 355 | LF |  |  | Scaled at 1"=30' (±10%). ISP pedestal location approximate — coordinate w/ ISP.
B2 | DB1 duct bank — MH1-1 to MH1-2 | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 | Scaled | 220 | LF |  |  | Scaled at 1"=30' (±10%).
B3 | DB1 duct bank — MH1-2 to HH1-2 (Bldg C / pedestrian gate) | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 / KN 3 | Scaled | 165 | LF |  |  | Future conduit connection to Bldg C; coordinate final HH location w/ security contractor.
B4 | DB1 duct bank — MH1-2 to HH1-4 (Bldg B) | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 / KN 4 | Scaled | 90 | LF |  |  | Coordinate final location w/ security contractor for connection to security gate.
B5 | DB1 duct bank — MH1-3 to MH1-4 | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 | Dimensioned | 123.1 | LF |  |  | Plan dim 123'-1".
B6 | DB1 duct bank — MH1-4 to HH1-3 (future Bldg B connection) | (2) 4" conduits, 1H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 / KN 2 | Dimensioned | 13.7 | LF |  |  | Plan dim 13'-8 1/4".
B7 | DB1 SUBTOTAL — (2) 4" PVC w/ MaxCell |  |  |  |  | 966.8 | LF
B8 | DB2 duct bank — MH1-2 to MH1-3 | (4) 4" conduits, 2H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 | Scaled | 120 | LF |  |  | Scaled at 1"=30' (±10%).
B9 | DB2 duct bank — MH1-3 to Bldg A entry | (4) 4" conduits, 2H x 2W | 4" PVC DB duct, ea. w/ (1) 4" 3-cell MaxCell innerduct; concrete-encased | TSN100 | Dimensioned | 21.4 | LF |  |  | Plan dim 21'-4 3/4" to building; additional 33'-10 3/4" continues inside Bldg A (building package).
B10 | DB2 SUBTOTAL — (4) 4" PVC w/ MaxCell |  |  |  |  | 141.4 | LF
B11 | DB3 duct bank — HH1-3 to HH1-5 | (2) 2" conduits, 1H x 2W | 2" PVC duct, ea. w/ (1) 2" 3-cell MaxCell innerduct; encasement assumed (no section) | TSN100 | Dimensioned | 101.5 | LF |  |  | 72'-x 1/4" diagonal + 29'-2 1/2" segments (partially obscured dim — verify 72' leg).
B12 | DB3 duct bank — HH1-5 to HH1-6 (east vehicle gate) | (2) 2" conduits, 1H x 2W | 2" PVC duct, ea. w/ (1) 2" 3-cell MaxCell innerduct; encasement assumed (no section) | TSN100 | Dimensioned | 197.3 | LF |  |  | 179'-7 1/4" + 17'-8 3/4". NOTE: overall dim 508'-8 3/4" also shown at HH1-6 does NOT reconcile — RFI.
B13 | DB3 SUBTOTAL — (2) 2" PVC w/ MaxCell |  |  |  |  | 298.8 | LF
| Subtotal B (priced lines) | [7 empty] | 0
C. TRENCH / ENCASEMENT / MISC (quantities driven by duct bank LF above)
C1 | Trench & backfill for telecom duct banks | 30" min cover; ≥6' deep under traffic | Excavate, bed, backfill, compact; detectable warning tape; below 50-yr freeze line | TSN100 GN 8/9 | Calc | 1407 | LF |  |  | Equals sum of all duct bank segments above.
C2 | Concrete encasement — DB1 runs | 16" H x 23" W section (2.56 SF) | 3000 psi concrete; 4-#4 longitudinal rebar; #3 wire hoops @18" OC; plastic spacers @4' OC | A8/TSN400 | Calc | 91.7 | CY |  |  | Qty = DB1 LF x 2.56 SF / 27. Reinforcement may vary w/ soil conditions per structural.
C3 | Concrete encasement — DB2 runs | 25" x 25" section (4.34 SF) | 3000 psi concrete; 4-#4 longitudinal rebar; #3 wire hoops @18" OC; plastic spacers @4' OC | A13/TSN400 | Calc | 22.7 | CY |  |  | Qty = DB2 LF x 4.34 SF / 27.
C4 | Concrete encasement — DB3 runs (assumed encased; no section drawn) | 14" x 8-1/2" envelope (0.83 SF) | 3000 psi concrete (assumed, matching DB1/DB2) | TSN100 sched. | Calc | 9.2 | CY |  |  | Qty = DB3 LF x 0.83 SF / 27. Verify concrete-encased vs. direct-buried (RFI-2).
C5 | Bonding conductor, power-to-telecom plant bond; bond metallic-sheath cables at each MH | #6 AWG min | Bare Cu bonding conductor per NEC/NESC (IEEE C2); MH bonding ribbon connections | TSN100 GN 3/12 | Allowance | 1 | LS
C6 | Pull string / mule tape in all conduits & innerduct cells | — | Polyester mule tape, 1,250 lb (assumed); empty conduits w/ 200-lb test pull string per TSN notes | TSN gen. notes | Allowance | 1 | LS
| Subtotal C | [7 empty] | 0
D. OSP CABLING (TSN300 site one-line)
D1 | OSP fiber — Bldg A to MH/HH system incl. coils for future connection at Bldg B/C and east gate handholes | 12-strand | OM4 50/125 multimode, OSP-rated (gel-free, assumed), green-dashed runs per TSN300 | TSN300 | Scaled | 1600 | LF |  |  | Routes + 20% slack + coils (QC: coiled for future connection at HH1s). Revise when cable schedule issued.
D2 | Fiber terminations, LIU/patch panel at Bldg A, testing & documentation | 12 strands | LC LIU/patch panel (assumed); OTDR + insertion loss testing, labeling per TIA-606 | TSN300; TSN001 matrix | Allowance | 1 | LS |  |  | Contractor per responsibility matrix (Div 27).
D3 | OSP copper backbone cabling — TBD (QC: 'Where is the OSP copper?') | Pair count TBD | OSP-rated copper backbone (type/size not shown at 65%) | TSN300 QC | Allowance | 1 | LS |  |  | Matrix lists copper backbone as Contractor scope but none shown on one-line — carry allowance / RFI.
D4 | ISP fiber & ISP telecom pedestal — BY ISP | Per ISP | ISP-furnished fiber & pedestal; contractor provides DB1 pathway (item B1) | TSN300; TSN001 matrix | By Others-NIC | 1 | LS
| Subtotal D | [7 empty] | 0
| TELECOM OSP TOTAL | [7 empty] | 0

## Security
SECURITY SYSTEMS TAKEOFF (Sheets TSY001, TSY002, TSY100, TSY101)
DOE Legacy Management – Site Improvement Package ¦ 764 Horizon Dr., Grand Junction, CO ¦ 65% Submittal (Issue 02 SEP 2026) ¦ Contract W9128F24D0010
Item | Description | Size | Type / Material / Model No. | Ref (Sheet / Detail / Keynote) | Basis | Qty | Unit | Unit Cost ($) | Extension ($) | Notes
A. FIELD DEVICES — GATES
A1 | Pedestal-mounted video intercom w/ integrated card reader, concrete footer & conduit | 48" above roadway; min 2" sq pedestal | Welded 316 stainless gooseneck pedestal, heavy wall; PoE video intercom + reader; 1" conduit for signal; footer to frost depth, 20" from curb | TSY100; A1/TSY101 | Counted | 2 | EA |  |  | East vehicle gates at HH1-5 & HH1-6. QC: locations updated per civil — verify against updated background.
A2 | Building-mounted video intercom w/ integrated card reader — vehicle gate at Bldg B | Mtg ht 3'-10" AFF (typ per TSY001) | Wall-mount video intercom/reader; 4-11/16" sq 2-device mud-ring box, 2-1/8" deep; (1) 1" C stub | TSY100; TSY001 sched. | Counted | 1 | EA
A3 | Building-mounted card reader — pedestrian gate (Bldg C area) | Mtg ht 3'-6" AFF (typ per TSY001) | Card reader; 4-11/16" sq 1-device mud-ring box, 2-1/8" deep; (1) 3/4" C stub | TSY100; TSY001 sched. | Counted | 1 | EA |  |  | QC: shift reader to wall mount at the gate; OSP-rated ACS cable keynote to be added.
A4 | Card reader at personnel swing gate (TSY101 inset, KN 7) — additional to A3? | Mtg ht 3'-6" AFF (typ) | Card reader in WP enclosure (see A8 rough-in) | TSY101 inset KN 7-9 | Counted | 1 | EA |  |  | Inset shows readers at swing gate (KN 8) & personnel swing gate (KN 9, gates per C-503). VERIFY overlap with A2/A3 before pricing.
A5 | Vehicle gate operator connection/interface (operator & gate by others — civil C-503) | — | Gate command wiring, dry-contact/relay interface to operator controller | TSY101 flow diag. | Counted | 3 | EA |  |  | VEH GATE 1/2/3 operators. 120V power JB by electrical (Site Electrical D1).
A6 | Vehicle exit loop w/ lead-in to gate operator | Loop size per operator mfr | Preformed or saw-cut inductive loop + sealant + lead-in | TSY101 flow diag. | Counted | 3 | EA
A7 | Gate position switch (DPS) on sliding gate | — | Magnet on gate + position switch on fence-post bracket; armored cable; WP single-gang box; 3/4" conduit to handhole | A7/TSY101 | Counted | 3 | EA |  |  | Assumed one per vehicle gate; verify sliding vs. swing gate count w/ C-503.
A8 | Access control rough-in at fence gates | (2) 1" conduits to SEC | WP sheet-metal enclosure for card reader; swinging gate lock & bracket; torx/peg tamper-resistant hardware | A13/TSY101; GN 18 | Counted | 2 | EA |  |  | Per access control gate rough-in detail (swing/personnel gates).
| Subtotal A | [7 empty] | 0
B. HEAD END (COMM 124, Bldg A) & PANELS
B1 | Access control panel ACP1 | Surface mount, 5'-0" AFF (TSY001 sched.) | ACP w/ enclosure & power supply, Div 28; mount to fire-rated plywood | G2/TSY101; TSY001 | Counted | 1 | EA
B2 | Access control panel ACP2 ('if necessary') | Surface mount, 5'-0" AFF | ACP w/ enclosure & power supply, Div 28 | G2/TSY101 | Counted | 1 | EA |  |  | Shown dashed / 'IF NECESSARY' — carry until panel count confirmed.
B3 | Equipment rack, COMM 124 | 12U | Wall/floor rack per detail | G2/TSY101 | Counted | 1 | EA
B4 | ACS server + access control software, licensing & commissioning | Rack-mount | ACS server, Div 28 contractor furnished/installed per matrix | G2/TSY101; TSY002 | Counted | 1 | LS
B5 | VIC (video intercom) master station | Desktop (TSY001 sched.) | Video intercom master station w/ (1) copper cable to switch; surface mount to desk | TSY101 flow diag. | Counted | 1 | EA |  |  | Video intercom system remains contractor scope per TSY002.
B6 | Security network switch — OWNER furnished/installed; coordination only | PoE | Owner network switch (matrix: owner/owner) | TSY002 matrix | By Others-NIC | 1 | EA
B7 | VSS (video surveillance) server — EXCLUDED (struck from TSY002 at 65%) | — | — | TSY002 | Excluded | 0 | EA |  |  | VSS head-end, cameras & cabling struck on matrix but still drawn on G2/TSY101 rack — VERIFY deletion before bid.
B8 | Surge protection devices & associated cabling (head end + field) | — | SPDs on OSP copper entering building + device circuits, Div 28 | TSY002 | Allowance | 1 | LS
| Subtotal B | [7 empty] | 0
C. CABLING (homeruns via telecom duct bank system to COMM 124)
C1 | OSP-rated access control cable to each card reader location | Composite/multi-conductor per spec 28 | OSP-rated ACS cable (reader/lock/DPS/REX composite assumed) | TSY100 QC notes | Allowance | 1800 | LF |  |  | 5 reader locations; homerun lengths estimated along duct routes + slack.
C2 | Extended-reach copper data cable to each intercom (3) | 4-pair, 22 AWG min | Extended-reach PoE-rated OSP copper data cable (per TSY101 riser note & QC keynote) | TSY101; TSY100 QC | Allowance | 1400 | LF |  |  | (3) cables per riser note. Verify length/bandwidth/PoE load/voltage-drop per mfr (GN 9) — east gate run ±600 LF.
C3 | ACS cables, ACP1/ACP2 to Bldg A doors/monitored devices — BUILDING PACKAGE | — | — | G2/TSY101 | By Others-NIC | 0 | LS |  |  | Interior building security in Building A package, excluded from site takeoff.
C4 | Testing, labeling, commissioning, software licensing — all site security systems; record drawings | — | Per TSY100 GN 8 & Div 28 | TSY002; TSY100 GN 8 | Allowance | 1 | LS
| Subtotal C | [7 empty] | 0
D. EXCLUSIONS (struck from TSY002 responsibility matrix at 65% — VERIFY)
D1 | Video surveillance cameras, mounting hardware, network cabling, head-end server & storage | — | — | TSY002 | Excluded | 0 | — |  |  | Struck through in red on matrix.
D2 | Intrusion detection system (head end, DPS/glass break/motion devices, cabling) | — | — | TSY002 | Excluded | 0 | — |  |  | Struck through in red on matrix.
D3 | Wireless access points & enclosures; servers/routers/firewalls/phones/computers | — | — | TSY002 | Excluded | 0 | — |  |  | Owner items / struck.
D4 | Emergency blue phones & associated cabling | — | — | TSY002 | Excluded | 0 | — |  |  | Struck through in red on matrix.
| SECURITY TOTAL | [7 empty] | 0

## Materials & Makes
MATERIALS, MAKES & MODELS — PROCUREMENT LIST
'Specified' = named on the 65% drawings. 'Basis-of-design (suggested)' = drawings silent — a common product meeting the drawn requirements, offered for pricing only; Div 26/27/28 specs govern. Qty cells link live to the takeoff tabs.
Cat. | Item | Size / Rating | Manufacturer | Model / Part No. | Spec Status | Qty | Unit | Notes
LIGHTING
L1 | Area luminaire EA1 (Type 3, backlight control, house-side shield) | 35' pole mt; 277V; 3000K/80CRI; P3 pkg | Lithonia Lighting (Acuity) | DSX1-LED-P3-30K-80CRI-BLC3-MVOLT-XXXX-PIR-SPD20KV-HS-EGSR-DDXX | Specified | 9 | EA | D-Series Size 1. Wattage/lumen columns blank on 65% schedule — per fixture submittal. XXXX = distribution/finish fields to complete.
L2 | Area luminaire EA2 (Type 5 wide) | 35' pole mt; 277V; 3000K/80CRI; P3 pkg | Lithonia Lighting (Acuity) | DSX1-LED-P3-30K-80CRI-T5W-MVOLT-XXXX-PIR-SPD20KV-EGSR-DDXX | Specified | 7 | EA | Plan symbol shows twin heads/pole — RFI-3.
L3 | Area luminaire EA3 (short-throw T1S, house-side shield) | 35' pole mt; 277V; 3000K/80CRI; P3 pkg | Lithonia Lighting (Acuity) | DSX1-LED-P3-30K-80CRI-T1S-MVOLT-XXXX-PIR-SPD20KV-HS-EGSR-DDXX | Specified | 2 | EA
L4 | Light pole, round straight steel or aluminum | 35'-0 nominal; drilled for D-Series arm | Valmont / RSA / Lithonia SSS (or equal) | Per luminaire mfr pole selector, EPA per wind load | TBD | 18 | EA | Pole make/finish NOT scheduled at 65% — coordinate w/ luminaire order; anchor bolts per mfr (2/ES601).
L5 | LED bollard EB1 (RADEAN) | 8-1/4" dia x 41-1/2" H; 277V; 3000K/80CRI | Lithonia Lighting (Acuity) — schedule says 'Luminis' | RADB-LED-P1-30K-SYM-PIR-BTT-BCF-HXX-DDXX | Specified | 6 | EA | RADB is Lithonia's RADEAN bollard (Luminis is a sister Acuity brand) — RFI-13 to correct schedule mfr.
L6 | Flagpole downlight EF1 (StarGazer) | Size M (flags to 15'x25'); 3000K; LED | Eagle Mountain Flag & Flagpole | SG-3K-EHS-M-XX (external halyard, stationary truck) | Specified | 3 | EA | Dark-sky downlight; remote drivers in buried WP box (ES101 KN 10).
L7 | WP enclosure for EF1 remote drivers | Burial/landscape rated, NEMA 4/6P (assumed) | TBD (per driver mfr) | — | TBD | 1 | EA | Verify enclosure & driver model w/ Eagle Mountain submittal.
SERVICE & POWER
P1 | Pad-mount transformer | 480/277V 3-ph; kVA TBD by utility | Xcel Energy | Per XE standards | By Others | 1 | EA | XE furnished/installed; pad & grounding by GC/EC.
P2 | Meter housing + CT cabinet | Per XE metering standard; NEMA 3R | Milbank / B-Line (or per XE approved list) | Per XE metering spec | BOD (suggested) | 1 | EA | EC furnishes/installs housing; XE sets meter (ES101 KN 4).
P3 | Exterior JB for gate operator power | Min 4-11/16" sq (NEC 314); NEMA 3R/4 | Hoffman / Wiegmann (or equal) | Galvanized steel, gasketed, stamped | BOD (suggested) | 3 | EA | Per ES101 KN 7; 2#10+1#10G, 3/4"C, 120V.
P4 | Ground rods & bonding | 5/8" x 8' (assumed); #6 bare Cu | ERICO / Harger (or equal) | Cu-clad rod + exothermic or irreversible compression | BOD (suggested) | 18 | EA | Rod size not on drawings — confirm Div 26 spec.
TELECOM OSP
T1 | Telecom maintenance hole MH1 | 8'-0" x 96" x 96"; base 9,275 lb / top 2,100 lb | Oldcastle / Jensen Precast (or regional precaster) | '4260' base + top deck per H1/TSN400 | TBD | 4 | EA | '4260' designation from detail — confirm precaster & traffic rating of cover.
T2 | Telecom handhole HH1 | 3'-0" x 24" x 48" | Hubbell/Quazite or Armorcast (or equal) | Polymer concrete box + slip-resistant bolted cover, ANSI Tier (non-deliberate traffic) | BOD (suggested) | 5 | EA | NOT vehicle-traffic rated per A1/TSN400 — keep out of pavement.
T3 | Duct bank conduit, 4" | 4" PVC Type DB/EB (concrete-encased) | Cantex / JM Eagle (or equal) | DB-60/DB-120 PVC duct | BOD (suggested) | 2499 | LF | Conduit-feet: DB1 LF x2 + DB2 LF x4 (live formula).
T4 | Duct bank conduit, 2" | 2" PVC | Cantex / JM Eagle (or equal) | Sch 40/DB PVC | BOD (suggested) | 598 | LF | DB3 LF x 2 conduits (live formula).
T5 | Fabric innerduct, 4" 3-cell | 4", 3-cell, w/ pull tapes | MaxCell | MaxCell 4" 3-cell (MXE4 series) | Specified | 2499 | LF | 'MaxCell' named on TSN100 duct bank schedule — one per conduit.
T6 | Fabric innerduct, 2" 3-cell | 2", 3-cell, w/ pull tapes | MaxCell | MaxCell 2" 3-cell (MXE2 series) | Specified | 598 | LF | One per DB3 conduit.
T7 | OSP fiber, 12-strand OM4 | 12F OM4 50/125 MM, OSP gel-free | Corning / OFS (or equal) | e.g. Corning ALTOS 012TU4-T4790D20 | BOD (suggested) | 1600 | LF | Type on TSN300 is generic '12-STRAND OM4 FIBER' — exact cable per Div 27 spec.
T8 | Fiber termination hardware @ Bldg A | 12F LC (assumed) | Corning CCH / Panduit (or equal) | LIU/patch panel + pigtails/splice | BOD (suggested) | 1 | LS | OTDR + IL testing per TIA; labeling per TIA-606.
T9 | Detectable warning tape & mule tape | 6" tape @12" above duct; 1,250-lb tape | Presco / Neptco (or equal) | "CAUTION BURIED TELECOM" + WP1250 mule tape | BOD (suggested) | 1407 | LF | Tape LF = trench LF (live).
SECURITY (Div 28 — models per spec; BOD offered where drawings silent)
S1 | Video intercom door/pedestal station w/ integrated reader | PoE; vandal/weather resistant; flush or pedestal | Aiphone (or equal) | IX Series 2 (e.g. IX-DVM) + reader module | BOD (suggested) | 3 | EA | Matches 'VIC' video intercom system & extended-reach PoE copper architecture (TSY101).
S2 | Video intercom master station | Desktop, video | Aiphone (or equal) | IX-MV7-* master | BOD (suggested) | 1 | EA | Desktop mount per TSY001 schedule.
S3 | Gooseneck pedestal, 316 SS | 48" above roadway; min 2" sq heavy wall | Pedestal PRO (or equal) | 316 SS gooseneck w/ template L-bolts x4 | BOD (suggested) | 2 | EA | Welded 316 SS required by A1/TSY101; footer to frost +20" from curb.
S4 | Card readers | Mullion/single-gang; 3'-6" AFF | HID (or equal) | Signo 20 / 20K | BOD (suggested) | 2 | EA | Reader tech (prox/SEOS/PIV) per DOE requirements — confirm; boxes per TSY001 schedule.
S5 | Access control panels ACP1/ACP2 | Surface mt 5'-0" AFF on fire-rated plywood | LenelS2 / Software House / Mercury-based (or equal) | Per Div 28 spec & DOE standard | TBD | 2 | EA | Head-end platform not named on drawings — owner standard governs.
S6 | Gate position switch (DPS) | Industrial gate switch w/ armored lead | Sentrol/Edwards 2500-series (or equal) | e.g. 2507A w/ magnet & bracket | BOD (suggested) | 3 | EA | Per A7/TSY101: magnet on gate, switch on fence post, WP 1-gang box, 3/4"C to HH.
S7 | Vehicle exit loops | Preformed loop size per operator mfr | EMX / Reno A&E (or equal) | Preformed loop + matching detector in operator | BOD (suggested) | 3 | EA | Gate operators (36' cantilever slide gates per C-502/C-503) by others.
S8 | Extended-reach PoE copper data cable | 4-pair, 22 AWG min, OSP-rated | Paige (or equal) | GameChanger PD2201EX (OSP) | BOD (suggested) | 1400 | LF | Named performance (extended-reach, 22AWG, PoE) on TSY101/QC — GameChanger is the common BOD; verify E gate run length vs. mfr limit.
S9 | OSP access control composite cable | Reader/lock/DPS/REX composite, OSP | Windy City Wire / West Penn (or equal) | Per Div 28 spec | BOD (suggested) | 1800 | LF
S10 | Equipment rack + SPDs | 12U rack; SPDs on OSP copper & device circuits | Middle Atlantic / CPI; DITEK (or equal) | 12U wall rack; DTK series SPD | BOD (suggested) | 1 | EA | Rack per G2/TSY101; SPD line item Security B8.

## Assumptions
ASSUMPTIONS, CLARIFICATIONS & EXCLUSIONS
1. DOCUMENTS USED
Drawing set 1 | DOE LM Site Improvement Package, 65% Submittal QC set, 43 sheets (Kenall project 8134, issue date Sept 02 2026) — sheets reviewed for this takeoff: G-001/002, CD101, E-001, ES101, ES601, TSN001/100/300/400, TSY001/002/100/101.
Drawing set 2 | Exterior Electrical/Comm QC extract, 10 sheets (ES101, ES601, TSN001/100/300/400, TSY001/002/100/101, plot date 8/25-8/26/2026). Sheets are identical in content to set 1 counterparts; tag counts verified to match in both sets.
Not available | Specifications (Div 26/27/28, 33 71 02), electrical one-line diagram, panel schedules, building 'A' package. Items referencing the one-line are carried as allowances; sizes marked '(assumed)' or 'TBD' pending these documents.
2. TAKEOFF METHODOLOGY
Counted | Device/fixture symbol and tag counts taken from plan text layer and verified visually on rendered sheets (both drawing sets agree).
Dimensioned | Lengths printed on TSN100 used verbatim (converted to decimal feet).
Scaled | Undimensioned routes measured off 150-dpi renders at the stated sheet scale 1"=30'-0" (±10% typical, ±25% for demo lines). The TSN100 graphic scale bar is wrong per QC comment ('scale bar does not match') — the title scale was used.
Allowance | Work that is clearly required but not yet drawn at 65% (site lighting branch circuits, security homerun cabling, OSP copper). Quantities are order-of-magnitude placeholders — revise at 95%.
Sizes & types | Size and Type/Material/Model columns are transcribed from the ES601 luminaire schedule, TSN100 site device & duct bank schedules, TSN400/TSY101/ES601 details, and TSY001 device schedule. Anything not stated on the drawings is marked '(assumed)' or 'TBD'.
Pricing | Unit costs intentionally left blank (yellow cells) for estimator input; all extensions and totals are live formulas.
3. GENERAL ASSUMPTIONS
A3.1 | Xcel Energy (XE) performs all primary work: boring/trenching, primary conduit & cable, transformer supply & connections, meter. Contract work starts at secondary landings + pad, grounding, meter housing (ES101 KN 4). Demarcation to be confirmed in Design Analysis (QC 11742742).
A3.2 | EA2 poles: plan symbol shows twin luminaire heads on a single pole; schedule lists one model. Takeoff carries 7 pole ASSEMBLIES — confirm heads/pole before pricing (14 luminaires if twin).
A3.3 | All 18 area-light poles are 35'-0" (schedule); foundations per 2/ES601 dimension schedule row '31'-40'' = 2'-0" dia x 9'-6" deep, 8-#5 verts.
A3.4 | Duct banks DB1/DB2 concrete-encased per TSN400 sections; DB3 assumed concrete-encased (no section drawn) — verify. Note the TSN100 duct bank schedule lists envelope dims (DB1 18"x10-1/2", DB2 18"x18", DB3 14"x8-1/2") that differ from the TSN400 encasement sections (23"x16", 25"x25") — encasement CY is computed from the TSN400 sections; see RFI-11.
A3.5 | MaxCell 3-cell fabric innerduct in EVERY duct bank conduit per TSN100 duct bank schedule (DB1/DB2: 4" cells; DB3: 2" cells) — included in duct bank unit rates.
A3.6 | Telecom trench: 30" min cover, below 50-yr freeze line, ≥6' below surface where vehicular traffic crosses (TSN100 GN 8/9); max 600' between MH/HH (GN 4); conduit sloped ≥0.4"/ft to MHs; 6"/12" separations from other utilities (GN 6/7).
A3.7 | Security homerun cabling routed through the telecom duct bank/MaxCell system to COMM 124 in Bldg A (TSY100 GN); no separate security duct bank carried. Security pathways in EMT or secured cable tray inside buildings (TSY100 GN 6).
A3.8 | Vehicle gates, fence, sliding/swing gate hardware are CIVIL scope (C-503); this takeoff carries only electrical/security devices, rough-in, loops and terminations at the gates.
A3.9 | Generator is existing government-owned; relocation + recertification testing by building electrical contractor (ES101 KN 8). Fuel, pad, and mechanical work excluded. Rating TBD from building package.
A3.10 | Site lighting controls are integral (PIR/dimming) + timeclock in Bldg A lighting control panel (building package); only interface wiring carried. Sequence: on 1 hr before business open, off within 1 hr after close, 10-min timeout, dim to 30%.
A3.11 | Assumed materials where drawings are silent: PVC Sch 40 for site branch conduits, THWN-2/XHHW-2 Cu conductors, 5/8"x8' Cu-clad ground rods, NEMA 3R/4 exterior enclosures, LC fiber terminations, 1,250-lb mule tape. All flagged '(assumed)' in the Type column.
4. EXCLUSIONS
E4.1 | All civil sitework: paving, grading, wet utilities (CU sheets), erosion control, fencing/gates, landscaping, flagpoles (poles themselves).
E4.2 | Fire protection (FP000) and all Building A/B/C interior electrical, telecom & security (building packages).
E4.3 | Video surveillance system (cameras, VSS server/storage, VSS cabling), intrusion detection, wireless access points, emergency blue phones — struck from TSY002 responsibility matrix at 65%. VERIFY before bid; TSY101 rack elevation still shows VSS server.
E4.4 | Owner-furnished items: network switches, routers/firewalls/servers/phones/computers, WAPs (TSY002/TSN001 matrices).
E4.5 | ISP scope: ISP fiber, ISP pedestal equipment, ISP network cabling (TSN001 matrix) — contractor provides pathway only.
E4.6 | Xcel Energy scope per A3.1: primary conduit/cable/trenching, transformer, meter device, existing utility transformer demolition.
E4.7 | Electric-service MH/HH/power poles: ES101 legend defines symbols but none appear on the 65% plan — none carried.
E4.8 | Hazmat survey/abatement, rock excavation, dewatering, winter conditions, premium time, taxes, bonds, escalation.
5. OPEN ITEMS / RECOMMENDED RFIs
RFI-1 | TSN100: overall dim 508'-8 3/4" at HH1-6 does not reconcile with segment dims (312 LF sum MH1-4→HH1-6; 435 LF from MH1-3). Confirm intended overall length / correct dims.
RFI-2 | DB3 duct bank: confirm concrete encasement vs. direct-bury (no section on TSN400) and confirm the partially-legible 72'-x diagonal dimension HH1-3→corner.
RFI-3 | Confirm EA2 = one or two luminaires per pole (plan symbol vs. schedule); complete wattage/lumen/CCT columns of luminaire schedule.
RFI-4 | Confirm final count/locations of card readers at swing & personnel gates (TSY101 inset vs. TSY100) and pedestrian-gate reader wall-mount change (QC).
RFI-5 | Confirm deletion of video surveillance & intrusion detection (TSY002 strikethroughs) vs. TSY101 rack still showing VSS server & 'to building cameras'.
RFI-6 | Site lighting circuiting, panel source, and photometric plan to be issued (QC) — allowances C10/C11/D2 must be re-quantified at 95%; confirm conduit/conductor sizes.
RFI-7 | HH1-1 appears on TSY100 but not TSN100 — confirm 6th handhole.
RFI-8 | OSP copper backbone shown in matrix but absent from TSN300 one-line ('Where is the OSP copper?' QC) — confirm scope, type and pair count.
RFI-9 | CD101: confirm counts/limits for UG telephone line removal, electric meter & comm JB demolition; confirm whether telco removes own aerial/UG plant.
RFI-10 | Relocated EA1 pole at generator (fire-truck access conflict, ES101 QC) — location change may affect circuit lengths.
RFI-11 | TSN100 duct bank schedule W x H values (DB1 18"x10-1/2", DB2 18"x18", DB3 14"x8-1/2") differ from TSN400 encasement sections (DB1 23"x16", DB2 25"x25") — confirm governing encasement dimensions for concrete quantities.
RFI-12 | Confirm transformer kVA, generator kW/recertification requirements, and secondary conductor/conduit schedule (one-line, building package).
RFI-13 | ES601 luminaire schedule lists EB1 manufacturer as 'Luminis', but model RADB-LED is Lithonia Lighting's RADEAN bollard (both Acuity brands) — confirm intended manufacturer/model.
RFI-14 | Complete the 'XXXX' placeholder fields in the DSX1 catalog strings (finish/options) and the blank wattage/lumen/CCT columns of the luminaire schedule.
6. MATERIALS & MAKES TAB
Method | The 'Materials & Makes' tab consolidates every product into a procurement list. 'Specified' items are named on the drawings (Lithonia DSX1 series, RADB/RADEAN bollard, Eagle Mountain StarGazer SG-EHS, MaxCell innerduct, '4260' precast MH). Where drawings are silent, a clearly-marked basis-of-design (BOD) suggestion is offered for pricing only — Div 26/27/28 specifications and DOE/owner standards govern final selection.
Verified | Manufacturer identities verified against current product literature: DSX1 = Lithonia D-Series Size 1 area luminaire (Acuity); RADB = Lithonia RADEAN bollard, 8-1/4" dia x 41-1/2" H (schedule's 'Luminis' appears to be an error — RFI-13); SG-3K-EHS-M = Eagle Mountain Flag & Flagpole 'StarGazer' dark-sky flagpole downlight, external-halyard stationary truck, size M for flags to 15'x25'.
Quantities | Qty cells on the Materials tab are live formulas linked to the takeoff tabs (green), including conduit-feet roll-ups (duct bank LF x conduits per bank). Changing a takeoff quantity updates the procurement list automatically.